## Sheet1
Vortex Enclosure Cooler - Sizing & Selection Worksheet
Fill out the requested data in the white cells
| Height (cm) | 50 | [5 empty] | short discription
| Width (cm) | 50 |  | Square Meter of Enclosure (m2) |  |  | 1.1 | NEMA 12: | Indoor: Dust Tight / Drip Tight
| Depth (cm) | 30 | [5 empty] | NEMA 4: | Outdoor: | Weatherproof / Washdown
[8 empty] | NEMA 4X: | Outdoor: | Weatherproof / Washdown, Corrosion Resistant
| Internal Temp. Now (°C) | 60 | Ambient Temp. Now (°C) | 60 |  | Delta T (°C) | 0
Vortex Cooler & Vortex A/C - BTUH Capacity
| Desired Internal Temp. (°C) | 45 | Worst Case Ambient (°C) | 60 |  | Delta T (°C) | 15 |  |  | AVAILABLE COMPRESSED AIR PRESSURE
|  |  | If internal and ambient temperatures are unknown, use dissipated heat in watts. |  |  |  |  | Enclosure Cooler Model Number |  | 4,1 BAR** |  | 5,5 BAR |  | 6,9 BAR
| Dissipated Heat in Watts | 25 | Additional BTU's | 85.3 |  | Total Delta T (°C) | 29 | with / without thermostat |  | BTUH | >21 °C | BTUH | >21 °C | BTUH | >21 °C
[8 empty] | 750 / 760 SCFM: 8 | NEMA 12 | 250 | 200 | 375 | 275 | 400 | 375
|  | Temp. Rise Due To Solar Radiation | [5 empty] | 740 / 730 15 | NEMA 12 | 600 | 375 | 775 | 525 | 900 | 700
|  | if enclosure is exposed to direct sunlight |  |  |  |  | Color Number | 790 / 780 25 | NEMA 12 | 750 | 625 | 1050 | 800 | 1500 | 1100
| Cabinet Color | Approx. Temp Rise |  | Number |  |  | 4 | 795 / 785 35 | NEMA 12 | 1200 | 900 | 1600 | 1250 | 2500 | 1600
| White |  | 4 | 1 |  |  |  | 7970 / 7870 2 x 35 | NEMA 12 | 2400 | 1800 | 3200 | 2500 | 5000 | 3200
| Cream |  | 7 | 2 |  | Total BTUH | 363.4284
| Yellow |  | 9 | 3 |  |  |  | 747 / 737 / 770-15H 15 | NEMA 4 | 600 | 375 | 775 | 525 | 900 | 700
| Light Gray |  | 14 | 4 |  |  |  | 770 25 | NEMA 4 |  |  | 1050 | 800 | 1500 | 1100
| Medium Gray |  | 22 | 5 |  |  |  | 797 / 787 25 | NEMA 4 | 850 | 700 | 1120 | 900 | 1700 | 1300
| Dark Gray |  | 25 | 6 |  | CAPACITIES |  | 770-35H 35 | NEMA 4 |  |  | 1600 | 1250 | 2500 | 1600
| Black |  | 27 | 7 |  |  |  | 797-35H / 787-35H 35 | NEMA 4 | 1200 | 900 | 1600 | 1250 | 2500 | 1600
| National Aluminum or |  | 14 | 8 |  |  |  | 7975 / 7875 2 x 35 | NEMA 4 | 2400 | 1800 | 3200 | 2500 | 5000 | 3200
Stainless Steel
[6 empty] | Additional | BTU's | 747SS / 737SS / 7715 15 | NEMA 4X | 600 | 375 | 775 | 525 | 900 | 700
The cabinet is: |  | Sealed and unvented. |  |  |  | provided by | fan(s). | 7725 25 | NEMA 4X |  |  | 1050 | 800 | 1500 | 1100
| * | Vented-fan cooled. ( |  |  | m3/h) | 0 |  | 797SS / 787SS 25 | NEMA 4X | 850 | 700 | 1120 | 900 | 1700 | 1300
|  | Vented-no fan. | [5 empty] | 7735 35 | NEMA 4X |  |  | 1600 | 1250 | 2500 | 1600
[8 empty] | 797SS-35H / 787SS-35H | NEMA 4X | 1200 | 900 | 1600 | 1250 | 2500 | 1600
[8 empty] | 7975SS / 7875SS / 7770 | NEMA 4X | 2400 | 1800 | 3200 | 2500 | 5000 | 3200
Note: If the compressed air supply is not dried to a - 40°C pressure dew point, devalue
|  | *Temperature of air entering enclosure (°C). | [5 empty] | capacities by 15%. Compressed air temperatures must not exceed 43°C.
| If fan cooled: | [6 empty] | If compressed air temperatures exceeds 43°C, ask for assistence.
*Temperature of air exiting enclosure (°C).
Note: "BTUH" : capacity when compressed air temperature does not exceed 21°C.
">21°C" : capacity when compressed air temperature exceeds 21°C.
Note: The models listed above which have a 770 prefix and the Vortex A/C models (listed in blue) all feature a
highly reliable mechanical thermostat to maintain cabinet temperatures within a range of approximately 27°-32°C.
** A minimum of 5,5 bar is required for proper operation of this thermostat.
Note on C3: Enter the Height of the cabinet in cm.
Note on C4: Enter the width of the cabinet in cm.
Note on H4: This is the surface of your enclosure in square meters based on the H, W & D that you enter.
Note on C5: Enter the depth of the cabinet in cm.
Note on C7: Enter the internal temperature of the cabinet. If unknown, go to the "Dissipated Heat in Watts" box.
Note on E7: Enter the temperature of the surrounding air. If unknown, go to the "Dissipated Heat in Watts" box.
Note on C9: Enter the temperature that you would like to maintain inside of the cabinet.
Note on E9: Enter the highest surrounding temperature that the cabinet will be exposed to.
Note on C11: If you don't know the internal temp and ambient temp, you need to obtain the dissipated watts rating for each component inside of the cabinet. This can usually be obtained from the manufacturer of the components. Keep in mind, this is not the total energy consumption of the components, but the amount of energy that is lost in the form of heat.
Note on H15: If the cabinet is exposed to direct sunlight, enter the number that corresponds to the color that matches the cabinet. If not exposed to direct sunlight, leave this box blank.
Note on H17: This is the total BTUH of cooling that you need to provide in order to maintain the desired temperature that you specified.
Note on E27: If your cabinet is fan cooled, enter the total SCFM rating(s) of fan(s) that are used to pull air through the cabinet. If not fan cooled, leave this box blank.
Note on G27: This is the total BTUH of cooling provided by the fans in your cabinet. This is included in the "Total BTUH" box. It is figured by multiplying the m3/h of the fan(s), by the temp difference of the air exiting and the air entering, by 1.08.
Note on G33: If your cabinet is fan cooled, enter the temperature of the air entering the enclosure. If not fan cooled, leave this box blank.
Note on G35: If your cabinet is fan cooled, enter the temperature of the air exiting the enclosure. If not fan cooled, leave this box blank